## PUMP ANL
Sl No | Date | Pumping From (GPS/ Tank No / Elevation ) | Lat | Long | Elevation ( From ) | Pumping to (GPS/ Tank No / Elevation ) | Lat | Long | Elevation , TO | Flow rate ( LPM), Repeat 4 times and write average. Can be done by with 20 L bucket and stopwatch . For the 10 m3 tanks cross check with total tank filling time | Flow rate , Field trial ( L/s ) | Flow rate , Corrected Minus 10% | Is it directly connected to tank or using transfer nodes in between? | Fuel consumption per hour, Write down in reamrks column how did you measure | Pump name | Is the pump running in full power? , YES/ NO | % power used while data record | Pumping distance ( Horizontal ) feet | Pumping distance ( Horizontal ) m | Image of the pump | Remarks
1 | 1:12 | TS:15 |  |  |  | TS:31 |  |  |  | 5 | 4 | 3.6 | TS:15:17:18:24:31 | 1 Hour:1.5 Letter | 25HP | NO | M | 2400 | 731.7073
2 | 1:12 | TS:31 |  |  | 81.2928 | Lagoon:1 |  | 98.7335 |  | 5.25 | 3.8095 | 3.4286 | TS:31 to lagoon:1 | 1 Hour :2 Letter | 25HP | YES | H | 600 | 182.9268
3 | 1:12 | TS:15 |  |  |  | TS:24 |  |  |  | 4.25 | 4.7059 | 4.2353 | TS:15:17:18:24 |  | 25HP | NO | M | 1500 | 457.3171
4 | 1:12 | TS:8 |  |  |  | TS:24 |  |  |  | 5 | 4 | 3.6 | TS:8:21:20:19:18:24 |  | 25HP | YES | H | 2100 | 640.2439
5 | 1:12 | TS:8 |  |  |  | TS:31 |  |  |  | 6.25 | 3.2 | 2.88 | TS:8:21:20:19:18:24:31 |  | 25HP | YES | H | 2700 | 823.1707
6 | 1:12 | TS:14 |  |  |  | TS:15 |  |  |  | 5.25 | 3.8095 | 3.4286 | TS:14:15 |  | Robin | NO | M | 600 | 182.9268
7 | 1:12 | TS:13 |  |  |  | TS:15 |  |  |  | 6 | 3.3333 | 3 | TS:13:14:15 |  | Robin | NO | M | 1500 | 457.3171
8 | 1:12 | TS:13 |  |  |  | TS:14 |  |  |  | 4.25 | 4.7059 | 4.2353 | TS:13:14 |  | Robin | NO | M | 750 | 228.6585
9 | 1:12 | TS:2 |  |  |  | TS:8 |  |  |  | 10 | 2 | 1.8 | TS:2:5:6:7:8 |  | Robin | YES | H | 2400 | 731.7073
10 | 1:12 | TS:2 |  |  |  | TS:6 |  |  |  | 6 | 3.3333 | 3 | TS:2:5:6 |  | Robin | NO | M | 7500 | 2286.5854
11 | 1:12 | TS:2 |  |  |  | TS:7 |  |  |  | 6.75 | 2.963 | 2.6667 | TS:2:5:6:7 |  | Robin | NO | M | 1600 | 487.8049
12 | 2:12 | N21.20695° E092.151447° | 21.2069 | 92.1514 | 81 | TS:3 | 21.207 | 92.151 | 87 | 4.75 | 4.2105 | 3.7895 | Lat St To TS:3 |  | Robin | NO | M | 250 | 76.2195 |  | Camp:3 block:3G bq:0262
13 | 2:12 | N21.20700° E092.14521° | 21.207 | 92.1452 | 81 | TS:22 | 21.2079 | 92.1452 | 73 | 4.25 | 4.7059 | 4.2353 | Lat St to TS:22 |  | Robin | NO | M | 400 | 121.9512 |  | Camp:4 block:4E sub.17
14 | 2:12 | N21.20987° E092°14880° | 21.2099 | 92.1488 | 85 | TS:7 | 21.2097 | 92.1488 | 97 | 3 | 6.6667 | 6 | Lat St to TS:7 |  | Robin | NO | M | 100 | 30.4878 |  | Camp:3 block:3B Sub:AA11
15 | 2:12 | N21.20705° E092.15105° | 21.207 | 92.151 | 87 | TS:7 | 21.2097 | 92.1488 | 97 | 6.25 | 3.2 | 2.88 | Ts:3:2:5:6:7 |  | Robin | Yes | H | 2000 | 609.7561
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167

## IFSTN
16 | 7:12 | Ts:21 N21.21121° E092.14581° EL:66 | Ts:20N21.21154° E092.14419° EL:60 | 3.5 | 5.7143 | Ts:21:20 | Robin | NO | M | 700F
17 | 7:12 | Ts:21 N21.21121° E092.14581° EL:66 | TS:19 N21.21060° E092.14333° EL:67 | 4.75 | 4.2105 | TS:21:20:19 | Robin | NO | M | 1200F
18 | 7:12 | Ts:21 N21.21121° E092.14581° EL:66 | Ts:18 N21.20968° E092.14213° EL:67 | 6 | 3.3333 | TS:21:20:19:18 | Robin | NO | M | 1800F
19 | 7:12 | Ts:21 N21.21121° E092.14581° EL:66 | Ts:24 N21.21128° E092.14089° EL:58 | 7.5 | 2.6667 | TS:21:20:19:18:24 | Robin | Yes | H | 2500F
20 | 8:12 | Lt N21.20737° E092.15270° EL:81 | TS:3 N21.20714° E092.15093° EL:63 | 5.5 | 3.6364 | Lt to ts:3 | Robin | yes | H | 700F | Camp:3 block:3G sub:34
21 | 8:12 | Ts:3 N21.20714° E092.15093° EL:63 | Ts:7 N21.20970° E092.14886° EL:86 | 6 | 3.3333 | Ts:3:2:5:6:7 | Robin | No | M | 2000F
22 | 8:12 | Lt N21.21051° E092.15094° EL:75 | ST N21.21063° E092.15060° EL:49 | 3.5 | 5.7143 | Lt to St | Robin | No | M | 200F | Camp:3 block:3B sub:31
23 | 8:12 | Ts:7 N21.20970° E092.14886° EL:86 | TS:8 N21.21131° E092.14727° El:72 | 6.75 | 2.963 | Ts:7 to Ts:8 | Robin | No | M | 800F
24 | 8:12 | Lt N21.20700° E092.14417° EL:96 | ST N21.20716° E092.14455° EL:72 | 4.75 | 4.2105 | Lt to St | Robin | No | M | 250F | Camp:4 block:4C sub:18

## Pumps
Pump Spec | Remarks | Image
Make-Robin Model Number: PT 305 Use: Water pump Engine: Robin EY20 Engine Type:4-stroke petrol, single-cylinder, air-cooled Engine Power:5.0 HP Inlet Size (inches)-2 Outlet size (inches)-3 Max Solid Size (mm)-30 Total Head (m)-22 Suction Lift (m)-8 Maximum Capacity (m3/hr)-60 | Used for latrine to tank transfer and tank to tank transfer
Make:Robin Model Number: PST80 - Trash pump Use:Slurry, sludge & sewerage Engine: Robin EY20 Engine Type:4-stroke petrol, single-cylinder air-cooled Engine Power:3.7kw (5.0HP) Inlet Size (inches):3 Outlet size (inches):2 Max Solid Size (mm):30 Total Head (m):22 Suction Lift (m):8 Maximum Capacity (m3/hr):38 | Used for latrine to tank transfer and tank to tank transfer. Can pump high viscous fluid / Slurry
Heavy duty clay pump , Engine – 25HP, Suction X Delivery- 3”X3” , Total Head 30m | Stationary base pump for long distance tank transfer with higher flowrate . This Engines are 25 HP / 22 HP powered , Pumps are from Ship , made locally , and few are from KSB Brand. Delivery head and others specs are theorotical as they are not produced by particula BRAND or alligned